## Help
Tools provided for pump curve parameters calculation
Pump curve generator
Based on the flow requirement a proper pump curve can be generated and used for energy demand prediction
Default solution, provides dataset for 3 pump size
Pump curve calibration
| Based on pump datasheet a real pump curve can be used for energy demand calculation |  | Based on the design flow demand from the process model, the actual pump curve coefficients will be calculated
| 1. | At least 3 known working point is needed at maximum frequency/rpm | The flow head is calculated in the pipe following the pump in the process model (diameter, length, roughness, etc. needed)
| 2. | VFD low limit frequency is needed
Pump curve is based on parabolic equations
VFD is estimated based on curve shifting
Pump operating point
Pump head = Flow/pipe head

## Curve generation
Input parameters |  | Small | Medium | Large |  |  | Flow [l/s] | Geometric/Static head | Dynamic head | Flow head | Pump head | Pump head at VFD limit | Efficiency | Efficiency at VFD limit | Power demand
Name | Symbol | Value | Value | Value | Unit | Comment | 0 | 6 | 0 | 6 | 10.37 | 4.416 | 0% | 0% | -
Target pumped flow from process model | Qpumped,target | 24000 | 48000 | 96000 | m3/d |  | 31.4815 | 6 | 0.0012844 | 6.0013 | 10.1488 | 4.1948 | 16.18% | 21.81% | 19.374
Geometric/Static head | Δhgeom | 6 | 8 | 10 | m |  | 62.963 | 6 | 0.0051378 | 6.0051 | 9.8604 | 3.9064 | 30.04% | 38.17% | 20.2714
Pipe dynamic head | dhl | 0.1 | 0.1 | 0.1 | m |  | 94.4444 | 6 | 0.01156 | 6.0116 | 9.5048 | 3.5508 | 41.6% | 49.09% | 21.1688
Required pump head | hloss,pump | 6.1 | 8.1 | 10.1 | m |  | 125.9259 | 6 | 0.020551 | 6.0206 | 9.0821 | 3.1281 | 50.84% | 54.56% | 22.0663
Installed pumps | ninstalled | 2 | 2 | 2 | pc |  | 157.4074 | 6 | 0.032111 | 6.0321 | 8.5923 | 2.6383 | 57.78% | 54.58% | 22.9637
Spare/Idle pumps from installed | nspare | 1 | 1 | 1 | pc |  | 188.8889 | 6 | 0.04624 | 6.0462 | 8.0353 | 2.0813 | 62.4% | 49.16% | 23.8611
Pump max efficiency | hmax | 65% | 65% | 65% | - |  | 220.3704 | 6 | 0.062938 | 6.0629 | 7.4111 | 1.4571 | 64.71% | 38.29% | 24.7586
Pump head capacity buffer | fhead | 70% | 70% | 70% | - |  | 251.8519 | 6 | 0.082204 | 6.0822 | 6.7198 | 0.76575 | 64.71% | 21.98% | 25.656
Pump flow capacity buffer | fflow | 70% | 70% | 70% | - |  | 283.3333 | 6 | 0.10404 | 6.104 | 5.9613 | 0.0072619 | 62.4% | 0.2246% | 26.5534
Turndown limit of Variable Frequency Drive | fVFD,limit | 70% | 60% | 60% | - |  | 314.8148 | 6 | 0.12844 | 6.1284 | 5.1356 | -0.81839 | 57.78% | -26.98% | 27.4509
Efficiency loss at Variable Frequency Drive | hVFD | 15% | 15% | 15% | - |  | 346.2963 | 6 | 0.15542 | 6.1554 | 4.2428 | -1.7112 | 50.84% | -59.63% | 28.3483
Sensitivity of Variable Frequency Drive | fsens,VFD | 80% | 80% | 80% | - |  | 377.7778 | 6 | 0.18496 | 6.185 | 3.2828 | -2.6712 | 41.6% | -97.72% | 29.2457
[7 empty] | 409.2593 | 6 | 0.21707 | 6.2171 | 2.2557 | -3.6983 | 30.04% | -141.3% | 30.1432
Pump curve parameters and specification | [6 empty] | 440.7407 | 6 | 0.25175 | 6.2518 | 1.1614 | -4.7926 | 16.18% | -190.2% | 31.0406
[7 empty] | 472.2222 | 6 | 0.289 | 6.289 | 0 | -5.954 | 0% | -244.7% | -
Pump curve calibration parameters |  | Small | Medium | Large
Name | Symbol | Value | Value | Value | Unit | Comment
Flow demand per pump | Qpump,pc | 277.7778 | 555.5556 | 1111.1111 | l/s | Only active considered
Pump efficiency at flow demand | hactual | 62.98% | 62.98% | 62.98% | -
Power demand of pump at flow demand | Pel,pump | 26.3951 | 70.0984 | 174.8132 | kW
Pump maximum flow at minimum head | Qmax | 472.2222 | 944.4444 | 1888.8889 | l/s
Variable Frequency Drive sensitivity | fsens,VFD | 80% | 80% | 80% | -
Pump parameters at maximum head, thus zero flow
Minimum flow | Qmin | 0 | 0 | 0 | l/s
Head at minimum flow | hmax | 10.37 | 13.77 | 17.17 | m
Efficiency at maximum head, minimum flow | hhmax | 0% | 0% | 0% | -
Pump parameters at operating point
Flow rate at operating point | Qop | 277.7778 | 555.5556 | 1111.1111 | l/s
Head at operating point | hop | 6.1 | 8.1 | 10.1 | m
Efficiency at operating point | hhop | 62.98% | 62.98% | 62.98% | -
Pump parameters at maximum flow, zero head
Flow rate at maximum flow, minimum head | Qmax | 472.2222 | 944.4444 | 1888.8889 | l/s
Minimum head | hmin | 0 | 0 | 0 | m
Efficiency at maximum flow, minimum head | hhmin | 0% | 0% | 0% | -
Pump parameters at maximum efficiency
Flow rate at maximum efficiency | Qhmax | 236.1111 | 472.2222 | 944.4444 | l/s
Head at maximum efficiency | hhmax | 7.0738 | 9.3931 | 11.7124 | m
Maximum efficiency | hmax | 65% | 65% | 65% | -
Pump curve parameters based on the 3 datapoint for headloss |  | Small | Medium | Large | h = ah,Q * Qpump2 + bh,Q * Qpump + ch,Q
Name | Symbol | Value | Value | Value | Unit | Comment
Calibration headloss curve coefficient a | ah,Q | -3.3881e-05 | -1.1247e-05 | -3.5061e-06 | -
Calibration headloss curve coefficient b | bh,Q | -0.0059606 | -0.0039574 | -0.0024673 | -
Calibration headloss curve intercept | ch,Q | 10.37 | 13.77 | 17.17 | -
Headloss curve turning point flow rate | Qtp | -87.963 | -175.9259 | -351.8519 | l/s
Headloss curve turning point headloss | hmax | 10.6322 | 14.1181 | 17.6041 | m
Pump curve parameters based on the 3 datapoint for efficiency |  | Small | Medium | Large | h = ah,Q * Qpump2 + bh,Q * Qpump + ch,Q
Name | Symbol | Value | Value | Value | Unit | Comment
Calibration efficiency curve coefficient a | ah,Q | -1.166e-05 | -2.9149e-06 | -7.2872e-07 | -
Calibration efficiency curve coefficient b | bh,Q | 0.0055059 | 0.0027529 | 0.0013765 | -
Calibration efficiency curve intercept | ch,Q | 0 | 0 | 0 | -
Flow rate at maximum efficiency | Qhmax | 236.1111 | 472.2222 | 944.4444 | l/s
Efficiency curve turning point: max efficiency | ηmax | 65% | 65% | 65% | -
VFD curve calibration parameters |  | Small | Medium | Large
Name | Symbol | Value | Value | Value | Unit | Comment
VFD parameters at max head, zero flow
Minimum flow with Variable Frequency Drive | Qmin,VFD | 0 | 0 | 0 | l/s
Efficiency at maximum head, minimum flow with Variable Frequency Drive | hhmax,VFD | 0% | 0% | 0% | -
VFD parameters at max efficiency
Flow rate with Variable Frequency Drive at maximum efficiency | Qhmax,VFD | 141.8109 | 315.9923 | 631.9846 | l/s
Maximum efficiency with Variable Frequency Drive | hmax,VFD | 55.25% | 55.25% | 55.25% | -
VFD parameters at max flow, zero head
Flow rate at VFD turndown limit at maximum flow, minimum head | Qmax,VFD | 283.6219 | 631.9846 | 1263.9693 | l/s
Efficiency at VFD turndown limit at maximum flow, minimum head | hhmax,VFD | 0% | 0% | 0% | -
Pump curve parameters for efficiency at VFD limit |  | Small | Medium | Large | h = ah,Q,VFD * Qpump2 + bh,Q,VFD * Qpump + ch,Q,VFD
Name | Symbol | Value | Value | Value | Unit | Comment
Calibration efficiency curve coefficient a at VFD limit | ah,Q,VFD | -2.7473e-05 | -5.5332e-06 | -1.3833e-06 | -
Calibration efficiency curve coefficient b at VFD limit | bh,Q,VFD | 0.0077921 | 0.0034969 | 0.0017485 | -
Calibration efficiency curve intercept at VFD limit | ch,Q,VFD | 0 | 0 | 0 | -
Parabola parameter calculation
Parabola parameter calculation
𝒂_(𝒉𝒆𝒂𝒅,𝑸)=(𝒉_𝒎𝒊𝒏−𝒉_𝒎𝒂𝒙)/((𝑸_𝒎𝒂𝒙−𝑸_𝒎𝒊𝒏 )×(𝑸_𝒎𝒂𝒙−𝑸_𝒘𝒑 ) )−(𝒉_𝒘𝒑−𝒉_𝒎𝒂𝒙)/((𝑸_𝒎𝒂𝒙−𝑸_𝒎𝒊𝒏 )×(𝑸_𝒎𝒂𝒙−𝑸_𝒘𝒑 ) )
𝒃_(𝒉𝒆𝒂𝒅,𝑸)=(𝒉_𝒘𝒑−𝒉_𝒎𝒂𝒙)/((𝑸_𝒘𝒑−𝑸_𝒎𝒊𝒏 ) )−(𝑸_𝒘𝒑−𝑸_𝒎𝒊𝒏 )×𝒂_(𝒉𝒆𝒂𝒅,𝑸)
𝒄_(𝒉𝒆𝒂𝒅,𝑸)=𝒉_𝒎𝒂𝒙−𝑸_𝒎𝒊𝒏^𝟐×𝒂_(𝒉𝒆𝒂𝒅,𝑸)−𝑸_𝒎𝒊𝒏×𝒃_(𝒉𝒆𝒂𝒅,𝑸)

## Pumpcalibration
Input parameters
Name | Symbol | Value | Unit | Comment |  |  | The entry of 3 points (Qi, Hi) is always required (*) in order to produce a nominal pump characteristic.
Target pumped flow from process model | Qpumped,target | 24000 | m3/d |  |  |  | For the 3 points, efficiencies can also be calibrated in to approximate an efficiency index - this results in the respective performance (**)
Geometric/Static head | Δhgeom | 6 | m
Pipe dynamic head | dhl | 0.1 | m |  |  |  | * A default line could be constructed at a desired operating point with known (Q1, H1) and standardized curves (default values for A and B).
Required pump head | hloss,pump | 6.1 | m | Required pump head at target flow
Installed pumps | ninstalled | 3 | pc |  |  |  | ** Alternatively, an efficiency curve can be constructed using a constant known electrical power. (Default values for eta)
Spare/Idle pumps from installed | nspare | 1 | pc | Spare pump to be used in case of failure
Target pumped flow per pump | Qpumped,target | 138.8889 | l/s | Only active considered |  |  |  | Flow [l/s] | Geometric/Static head | Dynamic head | Flow head | Pump head | Nominal efficiency | Pump head at VFD limit | Efficiency at VFD limit | Pump head at flow target | Efficiency at flow target | Power demand at flow target
[8 empty] | 0 | 6 | 0 | 6 | 16.9 | 31.22% | 6.76 | 0% | 14.9711 | 27.88% | 0
Pump curve parameters and specification | [7 empty] | 10.727 | 6 | 0.00014913 | 6.0001 | 16.4856 | 36.55% | 6.3456 | 15.65% | 14.5568 | 33.85% | 5.1245
[8 empty] | 21.454 | 6 | 0.00059652 | 6.0006 | 16.0259 | 41.36% | 5.8859 | 28.05% | 14.0971 | 39.16% | 8.6129
Pump curve calibration parameters for 3 point | [7 empty] | 32.181 | 6 | 0.0013422 | 6.0013 | 15.5209 | 45.63% | 5.3809 | 37.23% | 13.592 | 43.8% | 11.1858
Name | Symbol | Value at 1st | Value at 2nd | Value at 3rd | Unit | Comment |  | 42.9081 | 6 | 0.0023861 | 6.0024 | 14.9706 | 49.36% | 4.8306 | 43.17% | 13.0417 | 47.78% | 13.1875
Flow at the calibration points | Qcal,i | 60 | 110 | 170 | l/s |  |  | 53.6351 | 6 | 0.0037282 | 6.0037 | 14.3749 | 52.55% | 4.2349 | 45.87% | 12.446 | 51.1% | 14.8014
Head at the calibration points | hcal,i | 14 | 10.5 | 5 | m |  |  | 64.3621 | 6 | 0.0053687 | 6.0054 | 13.7339 | 55.21% | 3.5939 | 45.34% | 11.805 | 53.75% | 16.1327
Total efficiency at the calibration points | htotal,i | 54.2% | 60.55% | 52.81% | - |  |  | 75.0891 | 6 | 0.0073073 | 6.0073 | 13.0475 | 57.34% | 2.9075 | 41.57% | 11.1186 | 55.74% | 17.2434
Pumping power demand at the calibration points | Pel,pneu,i | 13 | 16 | 13.5 | kW |  |  | 85.8161 | 6 | 0.0095443 | 6.0095 | 12.3158 | 58.93% | 2.1758 | 34.56% | 10.387 | 57.06% | 18.1704
Motor power demand at the calibration points | Pel,motor,i | 13.6842 | 16.8421 | 14.2105 | kW |  |  | 96.5431 | 6 | 0.012079 | 6.0121 | 11.5388 | 59.98% | 1.3988 | 24.32% | 9.61 | 57.72% | 18.9335
Inverter power demand at the calibration points | Pel,inverter,i | 15.2047 | 18.7135 | 15.7895 | kW |  |  | 107.2701 | 6 | 0.014913 | 6.0149 | 10.7165 | 60.5% | 0.57651 | 10.84% | 8.7876 | 57.71% | 19.5398
Pump efficiency at the calibration points | hpumping,i | 63.39% | 70.82% | 61.77% | - |  |  | 117.9972 | 6 | 0.018045 | 6.018 | 9.8488 | 60.48% | -0.29116 | -5.869% | 7.92 | 57.04% | 19.9854
[8 empty] | 128.7242 | 6 | 0.021475 | 6.0215 | 8.9358 | 59.93% | -1.2042 | -25.82% | 7.007 | 55.71% | 20.2548
Calibration parameters for the 3 point | [7 empty] | 139.4512 | 6 | 0.025203 | 6.0252 | 7.9775 | 58.84% | -2.1625 | -49% | 6.0486 | 53.71% | 20.3181
Name | Symbol | Value | Unit | Comment |  |  |  | 150.1782 | 6 | 0.029229 | 6.0292 | 6.9739 | 57.22% | -3.1661 | -75.42% | 5.045 | 51.05% | 20.1256
VFD frequency at datapoints | ncalibration | 100% | - |  |  |  |  | 160.9052 | 6 | 0.033554 | 6.0336 | 5.9249 | 55.06% | -4.2151 | -105.1% | 3.996 | 47.72% | 19.5966
Viscosity correction | fviscosity | 0 | - |  |  |  |  | 171.6322 | 6 | 0.038177 | 6.0382 | 4.8306 | 52.37% | -5.3094 | -138% | 2.9017 | 43.73% | 18.5973
Degradation correction | fdegradation | 0 | - |  |  |  |  | 182.3592 | 6 | 0.043098 | 6.0431 | 3.6909 | 49.14% | -6.4491 | -174.1% | 1.762 | 39.08% | 16.8961
Inverter efficiency | ηel,inverter | 90% | - |  |  |  |  | 193.0863 | 6 | 0.048318 | 6.0483 | 2.5059 | 45.37% | -7.6341 | -213.5% | 0.57706 | 33.76% | 14.06
Motor efficiency | ηel,motor | 95% | - |  |  |  |  | 203.8133 | 6 | 0.053836 | 6.0538 | 1.2756 | 41.07% | -8.8644 | -256.1% | -0.65325 | 27.78%
VFD power loss correction at inverter | ηel,VFD,inverter | 5% | - |  |  |  |  | 214.5403 | 6 | 0.059652 | 6.0597 | 0 | 36.23% | -10.14 | -301.9% | -1.9289 | 21.13%
VFD power loss correction at motor | ηel,VFD,motor | 5% | -
VFD power loss correction at pumping | ηel,VFD,pumping | 10% | - | [11 empty] | 50% | 38.95% | 49.88% | 47.25%
[15 empty] | X | 77.9% | 99.75% | 94.5%
Calibration parameters for the VFD parameters | [14 empty] | freq | ηp(f) | ηM(f) | ηI(f)
Name | Symbol | Value | Unit | Comment | [10 empty] | 40% | 62.32% | 88.67% | 84%
VFD frequency at datapoints | ncalibration | 40% | - | [11 empty] | 52% | 65.33% | 91% | 86.21%
Inverter efficiency | ηel,inverter | 75.88% | - | [11 empty] | 64% | 67.37% | 92.52% | 87.65%
Motor efficiency | ηel,motor | 85.7% | - | [11 empty] | 76% | 68.84% | 93.59% | 88.67%
[15 empty] | 88% | 69.95% | 94.39% | 89.42%
Operating point operational parameters | [14 empty] | 100% | 70.82% | 95% | 90%
Name | Symbol | Value | Unit | Comment | [10 empty] | 50% | 64.91% | 90.68% | 85.91%
Frequency/rpm at flow target and flow headloss | nactual | 88.59% | -
Actual efficiency curve coefficient a | ah,Q,actual | -2.886e-05 | -
Actual efficiency curve coefficient b | bh,Q,actual | 0.0058769 | -
Actual efficiency curve intercept | ch,Q,actual | 27.88% | -
Headloss at target flow | Δhpump | 6.1 | m
Target flow | Qpumped,target | 138.8889 | l/s
Efficiency at target flow | ηactual | 53.83% | -
Power demand at target flow, head and rpm | Pel,pump | 15.4387 | kW
Pump curve calibration with VFD parameters
Name | Symbol | Value at 1st | Value at 2nd | Value at 3rd | Unit | Comment
Flow at the calibration points | Qcal,VFD,i | 0 | 57.2297 | 114.4595 | l/s
Head at the calibration points | hcal,i | 6.76 | 4.0251 | 0 | m
Total efficiency at the calibration points | htotal,i | 0 | 46.05% | 0 | -
Pumping power demand at the calibration points | Pel,pneu,i |  | 3.1911 |  | kW
Motor power demand at the calibration points | Pel,motor,i |  | 3.7237 |  | kW
Inverter power demand at the calibration points | Pel,inverter,i |  | 4.9072 |  | kW
Pump efficiency at the calibration points | hpumping,i |  | 70.82% |  | -
Pump curve parameters based on the 3 datapoint for headloss |  |  |  | h = ah,Q * Qpump2 + bh,Q * Qpump + ch,Q
Name | Symbol | Value | Unit | Comment
Calibration headloss curve coefficient a | ah,Q | -0.00019697 | -
Calibration headloss curve coefficient b | bh,Q | -0.036515 | -
Calibration headloss curve intercept | ch,Q | 16.9 | m
Headloss curve turning point flow rate | Qtp | -92.6923 | l/s | x coordinate of parabola turning point
Headloss curve turning point headloss | hmax | 18.5923 | m | y coordinate of parabola turning point
Pump curve parameters based on the 3 datapoint for efficiency |  |  |  | h = ah,Q * Qpump2 + bh,Q * Qpump + ch,Q
Name | Symbol | Value | Unit | Comment
Calibration efficiency curve coefficient a | ah,Q | -2.327e-05 | -
Calibration efficiency curve coefficient b | bh,Q | 0.0052262 | -
Calibration efficiency curve intercept | ch,Q | 31.22% | -
Flow rate at maximum efficiency | Qhmax | 112.2928 | l/s | x coordinate of parabola turning point
Efficiency curve turning point: max efficiency | ηmax | 60.56% | - | y coordinate of parabola turning point
Pump curve parameters based on the 3 datapoint for efficiency at VFD limit |  |  |  | h = ah,Q,VFD * Qpump2 + bh,Q,VFD * Qpump + ch,Q,VFD
Name | Symbol | Value | Unit | Comment
Calibration efficiency curve coefficient a at VFD limit | ah,Q,VFD | -0.0001406 | -
Calibration efficiency curve coefficient b at VFD limit | bh,Q,VFD | 0.016093 | -
Calibration efficiency curve intercept at VFD limit | ch,Q,VFD | 0% | -
Calibration headloss at VFD limit for 2nd point | hcal,VFD | 4.0251 | m | TRUE | Parabola coefficient crosscheck
| hmax | 0.90898 | m
Calibration flow at VFD limit for 2nd point | Qcal,VFD | 57.2297 | l/s | TRUE | Parabola coefficient crosscheck
Efficiency curve turning point: max efficiency | ηmax | 46.05% | -
Pump characteristic boundary parameters
Name | Symbol | Value top | Value min | Value op | Unit | Comment
Relative frequency | nrpm,i | 100% | 40% | 88.59% | -
Pumped flow at maximum efficiency | Qhmax,i | 112.2928 | 57.2297 | 101.8184 | l/s
Maximum efficiency | hmax,i | 60.56% | 46.05% | 57.8% | .
Efficiency curve intercept at high flow | Qmax,i | 273.6134 | 114.4595 | 243.3383 | l/s
Efficiency curve intercept at low flow | Qmin,i | -49.0279 | 0 | -39.7016 | l/s
Note on C84: peter.aichinger: YH is now no longer calculated using the C coefficient, but using the maximum of the original function. In the case of special curves, the C coordinate can already be very small, since approximation is only possible in the higher Q range. This means that at 100% turndown the C coordinate 0 will still be able to reach operating points. But that is implausible; when the pump is stopped, no flow is possible. Therefore, the maximum (and not the Y intersection) is moved to the origin. YH now refers to the maximum. Problems only arise if the maximum is exactly (!) In the zero point (Q).

## Sumo forms
Generated curve pump settings
Pump settings |  | Small | Medium | Large
Name | Symbol | Value | Value | Value | Unit
Installed pumps | ninstalled | 2 | 2 | 2 | pc
Minimum number of working pumps | nactive,min | 1 | 1 | 1 | pc
Pump curve settings |  | Small | Medium | Large
Name | Symbol | Value | Value | Value | Unit
Flow at the low flow calibration point | Qcal,low | 0 | 0 | 0 | l/s
Head at the low flow calibration points | hcal,Qlow | 10.37 | 13.77 | 17.17 | m
Total efficiency at the low flow calibration points | ƞcal,hlow | 0 | 0 | 0 | %
Flow at the operating flow calibration point | Qcal,op | 277.7778 | 555.5556 | 1111.1111 | l/s
Head at the operating flow calibration points | hcal,Qop | 6.1 | 8.1 | 10.1 | m
Total efficiency at the operating flow calibration points | ƞcal,hop | 62.9758 | 62.9758 | 62.9758 | %
Flow at the high flow calibration point | Qcal,high | 472.2222 | 944.4444 | 1888.8889 | l/s
Head at the high flow calibration points | hcal,Qhigh | 0 | 0 | 0 | m
Total efficiency at the high flow calibration points | ƞcal,hhigh | 0 | 0 | 0 | %
Flow at the operating flow calibration point with Variable Frequency Drive | Qcal,VFD,mid | 0 | 0 | 0 | l/s
Head at the operating flow calibration points with Variable Frequency Drive | hcal,VFD,mid | 4.416 | 6.9933 | 8.7201 | m
Total efficiency at the operating flow calibration points with Variable Frequency Drive | ƞcal,VFD,mid | 0 | 0 | 0 | %
Flow at the low flow calibration point with Variable Frequency Drive | Qcal,VFD,low | 141.8109 | 315.9923 | 631.9846 | l/s
Total efficiency at the low flow calibration points with Variable Frequency Drive | ƞcal,VFD,low | 55.25 | 55.25 | 55.25 | %
Flow at the high flow calibration point with Variable Frequency Drive | Qcal,VFD,high | 283.6219 | 631.9846 | 1263.9693 | l/s
Total efficiency at the high flow calibration points with Variable Frequency Drive | ƞcal,VFD,high | 0 | 0 | 0 | %
Variable Frequency Drive turndown limit | ncalibration,VFD | 30 | 40 | 40 | %
Datasheet calibrated pump settings
Pump settings |  | Calibrated
Name | Symbol | Value | Unit
Installed pumps | ninstalled | 3 | pc
Minimum number of working pumps | nactive,min | 1 | pc
Pump curve settings |  | Small
Name | Symbol | Value | Unit
Flow at the low flow calibration point | Qcal,low | 60 | l/s
Head at the low flow calibration points | hcal,Qlow | 14 | m
Total efficiency at the low flow calibration points | ƞcal,hlow | 54.1965 | %
Flow at the operating flow calibration point | Qcal,op | 110 | l/s
Head at the operating flow calibration points | hcal,Qop | 10.5 | m
Total efficiency at the operating flow calibration points | ƞcal,hop | 60.5476 | %
Flow at the high flow calibration point | Qcal,high | 170 | l/s
Head at the high flow calibration points | hcal,Qhigh | 5 | m
Total efficiency at the high flow calibration points | ƞcal,hhigh | 52.8105 | %
Flow at the operating flow calibration point with Variable Frequency Drive | Qcal,VFD,mid | 57.2297 | l/s
Head at the operating flow calibration points with Variable Frequency Drive | hcal,VFD,mid | 4.0251 | m
Total efficiency at the operating flow calibration points with Variable Frequency Drive | ƞcal,VFD,mid | 46.0505 | %
Flow at the low flow calibration point with Variable Frequency Drive | Qcal,VFD,low | 0 | l/s
Total efficiency at the low flow calibration points with Variable Frequency Drive | ƞcal,VFD,low | 0 | %
Flow at the high flow calibration point with Variable Frequency Drive | Qcal,VFD,high | 114.4595 | l/s
Total efficiency at the high flow calibration points with Variable Frequency Drive | ƞcal,VFD,high | 0 | %
Variable Frequency Drive turndown limit | ncalibration,VFD | 40 | %

## Parameter (hidden)
Misc. | label | variable | value | unit | name
| grav. | g | 9.81 | m/s² | g
| pressureN | p0 | 101325 | Pa | p0
| temperature0 | q0 | 273.15 | K | T0
| ind. gas constant | R | 8.3146 | J/mol.K | Ri
| temperatureN | Tst | 273.15 | K | Tst
Water | density | rw | 1000 | kg/m³ | dw
| dyn. visc. | hw | 0.001 | Pa.s | dvw
| kin. visc. | nw | 1e-06 | kg.m/s | kvw
| spez. heat | cpw | 4190 | J/kg.K | cpw
| surface tension | g | 0.07275 | Nm/m² | gamma
latent heat
Air (standard) | density | ra | 1.2925 | kg/m³ | da
| dyn. visc. | ha | 1.71e-05 | Pa.s | dva
| kin. visc. | na | 1.323e-05 | kg.m/s | kva
| spez. heat | cpa | 1005 | J/kg.K | cpa
| spez. Gas const. | Ra | 287 | J/kg.K | Ra
sludge (TS) | density | rTS | 1500 | kg/m³
| dyn. visc. | hTS |  | Pa.s
| kin. visc. | nTS |  | kg.m/s
| spez. heat | cpTS |  | J/kg.K
sludge (PS) | density | rPS | 1000 | kg/m³
4% | dyn. visc. | hPS |  | Pa.s
| kin. visc. | nPS |  | kg.m/s
| spez. heat | cpPS |  | J/kg.K
sludge (WAS) | density | rES | 1000 | kg/m³
4% | dyn. visc. | hES | 0.13 | Pa.s
| kin. visc. | nES | 0.00013 | kg.m/s
| spez. heat | cpES | 4190 | J/kg.K
sluge (FS) | density | rFS | 1500 | kg/m³
| dyn. visc. | hFS |  | Pa.s
| kin. visc. | nFS |  | kg.m/s
| spez. heat | cpFS |  | J/kg.K
US-Unit conversion
[6 empty] | liter per gallon | lpg | 3.7854 | lt/gal
Energy | calorific value CH4 | Ho_CH4 | 55.5 | [MJ/kg] | ho | gallon per liter | gpl | 0.26417 | gal/lt
| heat value CH4 | Hu_CH4 | 50.4218 | [MJ/kg] | hu | lb per kg | lpk | 2.205 | lb/kg
[6 empty] | kg per lb | kpl | 0.45351 | kg/lb
mol mass | N | M_N | 0.014 | kg/mol |  | HP per kW | hpk | 1.341 | HP/kW
| P | M_P | 0.03097 | kg/mol |  | kW per HP | kph | 0.7457 | kW/HP
| O | M_O | 0.016 | kg/mol |  | ft per meter | fpm | 3.2808 | ft/m
| Fe | M_Fe | 0.05585 | kg/mol |  | meter per ft | mpf | 0.3048 | m/ft
| S | M_S | 0.0321 | kg/mol |  | BTU per kJ | bpk | 0.94877 | btu/kJ
| C | M_C | 0.012 | kg/mol |  | kJ per BTU | kpb | 1.054 | kJ/btu
| H | M_H | 0.001 | kg/mol
| CH4 | M_CH4 | 0.016 | kg/mol
| H2O | M_H2O | 0.018 | kg/mol
| CO2 | M_CO2 | 0.044 | kg/mol
| Fe2(SO4)3 | M_Fe2(SO4)3 | 0.4 | kg/mol
| FePO4 | M_FePO4 | 0.15082 | kg/mol
| Fe(OH)3 | M_Fe(OH)3 | 0.10685 | kg/mol
| Ca2+ | M_Ca2+ | 0.04008 | kg/mol
| Ar | M_Ar | 0.039948 | kg/mol
| N2 | M_N2 | 0.028 | kg/mol
| O2 | M_O2 | 0.032 | kg/mol
gas constant | Ri |  | 8.3145 | J/mol.K
| RH2O |  | 461.9146 | J/kg.K
| RCH4 |  | 519.6539 | J/kg.K
| RCO2 |  | 188.965 | J/kg.K
| RO2 |  | 259.8269 | J/kg.K
| Rair |  | 287 | J/kg.K
| RAR |  | 208.1321 | J/kg.K
| RN2 |  | 296.9451 | J/kg.K
henry constant
k0H(O2) | 0.0013 | mol/kg.bar
K | 1500
Note on D33: peter.aichinger: Effect of ultrasound, low-temperature thermal and alkali pre-treatments on waste activated sludge rheology, hygienization and methane potential